## Slide 1
PC
◆ MONARCH · APC / CONTROLS UPDATE / 18 JUL 2026 SINCE 15 JUL
IGN and DI commands reach the cRIO 9049 FPGA — and killing any computer fails safe
Last update proved the warning chain trips correctly. Today: 1) commands from Python physically reach the FPGA (closest to ignition and injection hardware), and 2) deliberately crashing each controller now ends in a transition to Safe mode (emergency shutdown).
VERIFIED
12 / 12 ignition + injection channels live
From the Python console and the HMI: states go up one level at a time (by design), spark & injection unlocked only in idling/firing, all 12 FPGA channels active.
Panel E-STOP verified to override LabVIEW GUI/Python instantly.
A self-starting simulator build now boots a virtual engine with simulated crank and pressure signal.
FOUND → FIXED
We crashed each controller on purpose
Before: killing the supervisory cRIO changed nothing — screens stayed green, the engine kept scheduling ignition on stale permissions, indefinitely.
Now: the engine controller self-clamps to SAFE when its supervisor goes silent, and the operator screen computes its own health verdicts — displayed state = the most restrictive of every source it can verify alive. Re-tested by crashing both cRIOs: safe hold + honest screens, every time.
NEXT Oscilloscope session: verify spark & injection timing at the pins, sweep it live from Python · failure drills (watchdog, sync-loss, e-stop)
◆ Noble Thermodynamics — Argon Power Cycle Python ⇄ LabVIEW integration · SIL-1
PC
cRIO 9049
cRIO 9056
Heartbeat
Heartbeat