## Slide 1
MONARCH · CONTROLS → PYTHON MIGRATION · WHAT’S NEXT · 2026-07-07
1 / 5
The road ahead: from watching to commanding
The shadow phase proved Python decides correctly. The next phases give it hands — carefully: each increase in authority is built, then deliberately broken on the bench, and only granted after it fails safely and the team signs off.
PHASE B
Command path
wire the LabVIEW write
path, then drill it
UP NEXT
→
GATE: drills + sign-off
PHASE C
Bench command
Python drives modes &
setpoints — no engine
→
GATE: drills + sign-off
PHASE D
Procedures
automated sequences from
the team’s written steps
→
GATE: drills + sign-off
PHASE E
Commissioning
sequences drive cold flow
→ motoring → first fire
THE NEAR-TERM WORK, IN THREE NUMBERS
1
LABVIEW BUILD LEFT
the gateway write path (B3) — the only build between shadow mode and Python’s first commands; specified click-by-click
7
FAILURE DRILLS
we break the link every way we can think of, live — every failure must end in a rejection or a safe hold
0
AUTHORITY UNTIL THEN
Python’s writes stay ignored (source switch on UI) until every drill passes and the team signs off
Head start: the Python software for every phase — commander, operator tools, sequencing engine, warning rules — is already written and tested. The near-term work is LabVIEW wiring, bench drills, and team decisions.

## Slide 2
MONARCH · CONTROLS → PYTHON MIGRATION · WHAT’S NEXT · 2026-07-07
2 / 5
One LabVIEW build between shadow and command
Today the gateway only reads — it streams telemetry and politely acknowledges commands without acting. B3 teaches it to accept Python’s requests, with LabVIEW still validating every one, and a physical operator switch choosing who is in command.
WHAT GETS BUILT (3 SMALL PIECES)
▪ Two new shared variables — a place for the operator’s inputs while Python is in command, and a UI / PYTHON source switch that defaults to UI.
▪ The gateway command branch — parse each request, run a 6-check validation ladder (right command? within rate? right source? parses? in range? not clearing an e-stop?), then write — or reject with a stated reason.
▪ The HMI switch + single-writer rule — exactly one writer of the control settings at any moment; the operator owns the switch, and only the operator.
READY TO START
▪ Interface spec frozen with the team (ICD v0.2).
▪ Python + simulator sides built; 13 failure tests green.
▪ Every LabVIEW step written up node-by-node, ~half a day.
WHO WRITES, IN EACH MODE
SOURCE = UI (DEFAULT)
Operator UI → writes the control settings, exactly as today
Python → every command rejected: “source is UI”
SOURCE = PYTHON
Python → validated commands write the control settings
Operator UI → inputs become requests that Python reads
Either way: the 9056 state machine consumes the same variable and keeps clamping everything — the LabVIEW limiter never leaves the loop. And e-stop works from every surface, in every mode.

## Slide 3
MONARCH · CONTROLS → PYTHON MIGRATION · WHAT’S NEXT · 2026-07-07
3 / 5
Nothing gets authority until it fails safely: 7 drills
Before Python may command anything real, we try to break the link every way we can think of — live on the bench. Every failure must end the same two ways: a rejected request, or a safe hold. No exceptions, repeatably, witnessed.
1
Kill Python mid-command
cRIO clamps to SAFE within 5 s — the watchdog we just wired, re-proven through the full command path
2
Pull the network cable
same safe hold; the link re-establishes itself cleanly when the cable returns
3
Freeze the process
heartbeat stops changing while the socket stays up — watchdog still trips → SAFE
4
Send garbage
malformed JSON is rejected with a reason; the connection survives and keeps serving telemetry
5
Flood commands
more than 5 per second → rate limit trips, excess rejected — no queue, no lag
6
Flip the source mid-run
UI ↔ Python handover is bumpless — values match before the switch, nothing jumps
7
E-stop vs Python
e-stop from any surface always wins and latches; Python can request it but can never clear it
✔ PASS = all seven, repeatably, live
command → acknowledged → effect confirmed in telemetry; then joint sign-off closes Phase B
Why so much ceremony: this gate is the safety case. It demonstrates — not argues — that a dead, hung, or misbehaving Python can only ever cause a rejected request or a safe hold.

## Slide 4
MONARCH · CONTROLS → PYTHON MIGRATION · WHAT’S NEXT · 2026-07-07
4 / 5
Then Python takes the bench — supervised
Phase C makes Python the acting supervisor for bench operation — real authority against the real controllers, no engine hardware — while the LabVIEW clamp stays permanently underneath and the operator keeps an instant way back.
WHAT CHANGES
▪ Python drives mode requests and setpoints once per second through the command path Phase B just proved.
▪ The operator keeps the LabVIEW HMI: monitoring, e-stop, and the source switch — one flip hands control back to the UI, bumplessly.
▪ The shadow comparison now runs in reverse: Python predicts what the LabVIEW limiter will allow, and any disagreement raises an alarm immediately.
HOW WE’LL KNOW IT WORKS
▪ Soak runs: hours-long bench sessions with faults injected on purpose — no drift, no resource leaks, clean reconnects every time.
▪ Exit test: one scripted session — mode walks, setpoint changes, forced warnings, e-stop, kill-Python-and-recover — runs entirely under Python command with zero unsafe outcomes and zero unexplained limiter divergences.
WHY THIS PHASE MATTERS
It converts trust from theory to track record. Shadow mode proved the decisions; Phase B proves the failure modes; Phase C accumulates supervised operating hours. By the time automated sequences arrive (Phase D), Python isn’t a new component anymore — it’s the supervisor the bench has already been running under.

## Slide 5
MONARCH · CONTROLS → PYTHON MIGRATION · WHAT’S NEXT · 2026-07-07
5 / 5
What we need from the team — and where this lands
INPUTS THAT UNBLOCK THE NEXT PHASES
▪ Operating-procedure sheets (blocks Phase D)
cold start, purge, motoring → light-off, shutdown, vent & recovery, misfire recovery — as informal notes or the template sheets; they become tested, automated sequences. This is the critical path.
▪ Real numbers (blocks Phase E)
warning thresholds and time windows (“X low for Y s in state Z ⇒ act”) and operating-point tables — the engines are built and waiting for values.
▪ Two joint decisions
where the UI / PYTHON switch lives on the HMI, and the sign-off review at each authority gate (B exit is the first).
THE DESTINATION
Sequences drive commissioning itself
cold flow → motoring → first fire, each step a written, tested, repeatable procedure — not a one-off manual run
Non-combustion sequences go first
venting, purge, working-fluid checks, thermal warm-up — already drafted, and exactly what commissioning needs earliest
Every capability earns its place
nothing is unlocked until its bench drill passes — the same rule from day one, all the way up
The rule that never changes: LabVIEW/cRIO keeps the hardware, the interlocks and the safe fallback — permanently, through every phase on this roadmap. Python only ever asks; LabVIEW checks every request; if Python disappears, the system safe-holds.